SECTION 08 90 00

LOUVERS & VENTS

PART 1 GENERAL

  - SECTION INCLUDES

- Extruded aluminum stationary louvers.

1.02	RELATED SECTIONS *NOTE TO SPECIFIER* Delete sections not applicable.

- Section 03 30 00 – Cast-In-Place Concrete

- Section 04 20 00 – Unit Masonry

- Section 05 10 00 – Structural Metal Framing

- Section 06 10 00 – Rough Carpentry

- Section 07 42 13 – Metal Wall Panels

- Section 07 60 00 – Flashings and Sheet Metal

- Section 07 92 00 – Joint Sealants

- Section 09 91 00 – Painting

1.03	REFERENCES *NOTE TO SPECIFIER* Delete references not applicable.

- AAMA 2604 – High Performance Organic Coatings on Architectural Extrusions and Panels.

- AAMA 2605 – High Performance Organic Coatings on Architectural Extrusions and Panels.

- AMCA 500-L – Test Methods for Louvers.

- AMCA 511 – Certified Ratings Program for Air Control Devices.

- ASCE 7 – Minimum Design Loads for Buildings and Other Structures

- ASTM B209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

- ASTM B221 – Standard Specifications for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

- ASTM D822 – Standard Practice for Filtered Open-Flame Carbon-Arc Exposure of Paint and Related Coatings.

- ASTM D4214 – Standard Test Method for Evaluating the Degree of Chalking of Exterior Paint Films.

- ASTM D2244 – Standard Test Method for Calculation of Color Differences from Instrumentally Measured Color Coordinates.

- ASTM E330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights, and Curtain Walls by Uniform Static Air Pressure Difference.

- Living Building Challenge – Red List Chemicals.

1.04	SUBMITTALS

- Submit under provisions of Section 01 30 00

- Product Data: For each product to be used, including:

      - Manufacturer’s product data including performance data.

      - Installation Instructions

      - Maintenance and Operations Manuals

      - Health Product Declarations (HPDs) and Declare Labels.

- Shop Drawings

- Submit shop drawings indicating materials, construction, dimensions, accessories, and installation details.

D.   Samples

1.   Submit color chip sample for units with factory-applied paint.

1.05	QUALITY ASSURANCE

- Manufacturer Qualifications:

- The manufacturer shall have implemented the management of quality objectives, continual improvement, and monitoring of customer satisfaction to assure that customer needs and expectations are met.

- Manufacturer shall have International Living Future Institute (ILFI) Just Label or equivalent.

- Production Qualifications:

- Louvers shall be licensed to bear AMCA Certified Ratings Seal.  Ratings based on tests and procedures performed in accordance with AMCA 511 and comply with AMCA Certified Ratings Program.  AMCA Certified Ratings Seal applies to air performance and water penetration ratings.

1.06	DELIVERY, STORAGE, AND HANDLING

- Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

- Storage:  Store materials in a dry area indoors, protected from damage and in accordance with manufacturer’s instructions.

- Handling:  Protect materials and finishes during handling and installation to prevent damage

- Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.

1.07	PROJECT CONDITIONS

- Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by the manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer’s absolute limits.

- Field Measurements:  Verify actual dimensions of openings by field measurements before fabrication.  Coordinate field measurements and fabrication schedule with construction progress to avoid construction delays.

1.08	WARRANTY

- Manufacturer shall provide a standard limited warranty for louver systems for a period of 1 year from date of installation, no more than 18 months after shipment from manufacturing plant.  When notified in writing from the Owner of a manufacturing defect, manufacturer shall promptly correct deficiencies without cost to the owner.

*NOTE TO SPECIFIER* If fluorpolymer finish is not required delete below paragraph

- Manufacturer shall provide 20 year limited warranty for fluoropolymer-based finish on aluminum substrates.

- Finish Coating shall not peel, blister, chip, crack, or check.

- Chalking, fading, or erosion of finish when measured by the following tests:

  - Finish coating shall not chalk in excess of 8 numerical ratings when measured in accordance with ASTM D4214.

  - Finish coating shall not change color or fade in excess of 5 NBS units as determined by ASTM D2244 and ASTM D822

  - Finish coating shall not erode at a rate in excess of .01 mils/year confirmed by Florida test samples.

PART 2 PRODUCTS

  - MANUFACTURER

- Industrial Louvers Inc. (ILI) - Contact: 511 South 7th Street, Delano, MN 55328; Telephone: (763) 972-2981; Fax: (763) 972-2911.

- Other Available Manufacturers – subject to compliance with requirements stated within.

- (list acceptable equals by name)

##### EXTRUDED ALUMINUM WEATHER RESISTANT LOUVERS

A.	Fabrication:

- Model: 450XP

- Frame:

  - Frame Depth: 4 inches (101.6 mm)

  - Material: Extruded aluminum, 6063-T6

  - Wall Thickness: 0.081 inch (2.1 mm), nominal

- Blades:

  - Style: Horizontal

  - Material: Extruded aluminum, 6063-T6

  - Wall Thickness: 0.081 inch (2.1 mm), nominal

  - Angle: 40 degrees

  - Centers: 5 inches (127 mm), nominal

B.	Performance Data:

- Performance Ratings: Product must be licensed to bear the AMCA Certified Ratings Seal for water and Air Performance.

  - Based on testing 48 inches by 48 inches (1219 mm by 1219 mm) size unit in accordance with AMCA 500-L

- Free Area: 50.9% (8.15 sq.ft.)

- Water Penetration: Maximum of .01 ounces at an air flow of 818 FPM

- Static Pressure Loss: Not more than .15 inch of water gauge at an air flow of 870 FPM free area velocity.

##### 2.03	LOUVER ACCESSORIES

*NOTE TO SPECIFIER* Please delete accessories not required

A.	Exterior Aluminum Sill: Provide sill flashing of same material and finish as louvers where indicated on the drawings.

B.	Louver Screens: Provide framed removable, re-wire-able screens for exterior louvers.

*NOTE TO SPECIFIER* Please delete screens not required

1.	Bird Screen:

- Aluminum: Aluminum, ½ inch by 0.063 inch (12.7 mm by 1.6 mm), expanded, flattened.

- Stainless Steel: Stainless Steel, ½ in by 16 ga. (12.7 mm x 1.6 mm), welded

- Stainless Steel: Stainless Steel, ½ in by 19 ga. (12.7 mm x 1.1 mm), welded

2.	Insect Screen:

- 18 x 14 aluminum charcoal mesh 0.011 inch (0.28 mm) diameter wire.

- 18 x 18 mesh stainless steel 0.009 inch (0.23 mm) diameter wire.

C.	Blank Off Panels:

*NOTE TO SPECIFIER* Please delete blank off panels not required

  - Non-Insulated Blank Off Panels factory installed with removable screws and foam tape gaskets:

*NOTE TO SPECIFIER* Please select one of the choices below if required

    - 0.040 inch (1 mm) aluminum sheet

    - 0.050 inch (1.3 mm) aluminum sheet

    - 0.060 inch (1.5 mm) aluminum sheet

    - 0.080 inch (2 mm) aluminum sheet

    - 0.125 inch (3.2 mm) aluminum sheet

  - Insulated Blank Off Panels factory installed with removable screws and foam tape gaskets:

*NOTE TO SPECIFIER* Please select one of the choices below if required

    - 1 inch (25 mm) thick and to be faced on both sides with 0.032 inch (0.81 mm) thick aluminum sheet.  Panels to be fabricated with rigid fiberboard core having an R-Value of 4.  Panel perimeter frame to be a 0.063 inch (1.6 mm) thick extruded aluminum Z shape.  Panels to be finished to match louvers on one side only.

    - 2 inch (51 mm) thick and to be faced on both sides with 0.032 inch (0.81 mm) thick aluminum sheet.  Panels to be fabricated with rigid fiberboard core having an R-Value of 8.  Panel perimeter frame to be a 0.063 inch (1.6 mm) thick extruded aluminum Z shape.  Panels to be finished to match louvers on one side only.

2.04	FABRICATION

##### A.	Fabrication Requirements:

1.	Performance: Fabricate as required for optimum performance with respect to water penetration, strength, durability, and appearance.

2.	Size: Fabricate louvers in walls to meet dimensions indicated on Contract Documents.

  - Field Measurement: Verify size, location, and placement of louvers before fabrication.

  - Shop Assembly:

- Fabricate to minimize field adjustments, splicing, mechanical joints and field assembly of units.

- Preassemble units in shop to greatest extent possible and disassemble as necessary for shipping and handling.

- Clearly mark units for reassemble and coordinated installation.

  - Accessories: Include supports, anchorages and accessories required for complete assembly.

  - Vertical Mullions: Provide vertical mullions of type and spacing indicated but not further apart than recommended by the manufacturer.

  - Horizontal Mullions: Provide horizontal mullions at horizontal joints between louver units except where continuous vertical assemblies are indicated.

  - Connections: Join frame and blade members to one another by mechanical fastener, except where field bolted connections between frame members are made necessary by size of louvers.

  - Spacing: Maintain equal blade spacing to produce uniform appearance.

##### 2.06	FINISHES (FACTORY)

A.	General: Comply with NAAMM “Metal Finishes Manual” for finish designations and application recommendations, except as otherwise indicated.  Apply finishes in factory.  Protect finishes on exposed surfaces prior to shipment.  Remove scratches and blemishes from exposed surfaces that will be visible after completing finishing process.  Provide color as indicated or, if not otherwise indicated, as selected by architect.

*NOTE TO SPECIFIER* Please delete finishes not required

B.	Standard mill finish.

C.	Prime Coat:

- Apply alkyd prime coat following chemical cleaning and pretreatment.

- Primer preparation for field painting

D.	Fluorocarbon Two Coat Coating

- Coating shall conform to AAMA 2605.

- Louvers to be finished with a minimum 1.0 mil (0.025 mm) thick full strength 70% resin, 2 coat Fluoropolymer system.

- All aluminum shall be thoroughly cleaned, etched, and given a chrome-free conversion pretreatment before application of coating. Coatings shall be ILFI LBC Red List Declared.

E.	Fluorocarbon Three Coat Coating

- Coating shall conform to AAMA 2605.

- Louvers to be finished with a minimum 1.4 mil (0.035 mm) thick full strength 70% resin, 3 coat Fluoropolymer system.

- All aluminum shall be thoroughly cleaned, etched, and given a chrome-free conversion pretreatment before application of coating. Coatings shall be ILFI LBC Red List Declared.

F.	Clear Anodize

- Class I Clear Anodize

  - Comply with Aluminum Association AA-C22A41.  Clear anodized finish 215-R1.

  - Apply finish following chemical etching and pretreatment

  - Minimum thickness: 0.7 mils (0.018 mm).

- Class II Clear Anodize

  - Comply with Aluminum Association AA-C22A31.  Clear anodized finish 204-R1

  - Apply finish following chemical etching and pretreatment

  - Minimum thickness: 0.4 mils (0.01 mm)

G.	Color Anodize

- Class I Bronze Anodize

  - Light, Medium, Dark, Champagne

  - Comply with Aluminum Association AA-C2242 or AA-C2244.

  - Apply finish following chemical etching and pretreatment

  - Minimum thickness: 0.7 mils (0.018mm).

- Class I Black Anodize

  - Comply with Aluminum Association AA-C2242 or AA-C2244.

  - Apply finish following chemical etching and pretreatment

  - Minimum thickness: 0.7 mils (0.018mm).

PART 3 EXECUTION

3.01	EXAMINATION

- Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.

- Proceed with installation only after unsatisfactory conditions have been corrected.

##### PREPARATION

- Clean opening thoroughly prior to installation

- Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

##### 3.03	INSTALLATION

- Install louvers at locations as indicated on the drawings and in accordance with the manufacturer’s instructions.

- Install louvers plumb, level, in plane of wall, and in alignment with adjacent work.

- Install joint sealants as specified in Section 07 90 00.

3.04	CLEANING

- Clean louver surface in accordance with manufacturer’s instructions.

- Touch-up paint, repair or replace damaged products before Substantial Completion.