SECTION 10705

EXTERIOR SUN CONTROL DEVICES

PART 1 GENERAL

  - SECTION INCLUDES

- Extruded aluminum stationary exterior sun control devices.

  - RELATED SECTIONS *NOTE TO SPECIFIER* Delete sections not applicable.

- Section 03 30 00 – Cast-In-Place Concrete

- Section 04 20 00 – Unit Masonry

- Section 05 10 00 – Structural Metal Framing

- Section 06 10 00 – Rough Carpentry

- Section 07 42 13 – Metal Wall Panels

- Section 07 60 00 – Flashings and Sheet Metal

- Section 07 92 00 – Joint Sealants

- Section 09 91 00 – Painting

  - REFERENCES *NOTE TO SPECIFIER* Delete references not applicable.

- AAMA 2604 – High Performance Organic Coatings on Architectural Extrusions and Panels.

- AAMA 2605 – High Performance Organic Coatings on Architectural Extrusions and Panels.

- ASCE 7 – Minimum Design Loads for Buildings and Other Structures

- ASTM B209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

- ASTM B221 – Standard Specifications for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

- ASTM D822 – Standard Practice for Filtered Open-Flame Carbon-Arc Exposure of Paint and Related Coatings.

- ASTM D4214 – Standard Test Method for Evaluating the Degree of Chalking of Exterior Paint Films.

- ASTM D2244 – Standard Test Method for Calculation of Color Differences from Instrumentally Measured Color Coordinates.

- ASTM E330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights, and Curtain Walls by Uniform Static Air Pressure Difference.

- Living Building Challenge – Red List Free.

  - PERFORMANCE REQUIRMENTS

- Provide sun control devices which have been manufactured, fabricated and installed to withstand loads from ASCE – 7, or local requirements of Authority Having Jurisdiction.

- Sun control devices shall be designed to perform under conditions herein or required by site conditions with no permanent damage to or deforming of the sunshade blades or assembly, noise or metal fatigue caused by sunshade blade rattle or flutter, or permanent damage to fasteners or anchors.

  - SUBMITTALS

- Submit under provisions of Section 01 30 00

- Product Data: For each product to be used, including:

  - Manufacturer’s product data including performance data.

  - Installation Instructions

  - Maintenance and Operations Manuals

  - Health Product Declarations (HPDs) and Declare Labels

- Shop Drawings

  - Submit shop drawings indication materials, construction, dimensions, accessories, and installation details.

- Samples

  - Submit color chip samples for units with factory-applied paint.

1.06	QUALITY ASSURANCE

- Manufacturer Qualifications:

  - The manufacturer shall have implemented the management of quality objectives, continual improvement, and monitoring of customer satisfaction to assure that customer needs and expectations are met.

  - Manufacturer shall have International Living Future (ILFI) Just Label or equivalent.

1.07	DELIVERY, STORAGE & HANDLING

- Delivery: Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer and material

- Storage: Store materials in a dry area indoors, protected from damage and in accordance with manufacturer’s instructions.

- Handling: Protect materials and finishes during handling and installation to prevent damage

- Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.

1.08 	PROJECT CONDITIONS

- Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by the manufacturer for optimum results.  Do not install products under environment conditions outside the manufacturer’s absolute limits.

- Field Measurements: Verify actual measurements of openings by field measurements before fabrication.  Coordinate field measurements and fabrication schedule with construction progress to avoid construction delays.

1.09	WARRANTY

- Manufacturer shall provide a standard limited warranty for sun control systems for a period of 1 year from date of installation, no more than 18 months after shipment from manufacturing plant.  When notified in writing from the Owner of a manufacturing defect, manufacturer shall promptly correct deficiencies without cost to the owner.

*NOTE TO SPECIFIER* If fluorpolymer finish is not required delete below paragraph

- Manufacturer shall provide 20 year limited warranty for fluoropolymer-based finish on aluminum substrates

  - Finish coating shall not peel, blister, chip, crack, or check.

  - Chalking, fading, or erosion of finish when measured by the following tests:

    - Finish coating shall not chalk in excess of 8 numerical ratings when measured in accordance with ASTM D4214.

    - Finish coating shall not change color or fade in excess of 5 NBS units as determined by ASTM D2244 and ASTM D822

    - Finish coating shall not erode at a rate in excess of .01 mils/year confirmed by Florida test samples.

PART 2 PRODUCTS

  - SUN CONTROL DEVICES

- Design basis: Sun Control Devices as manufactured by Industrial Louvers Inc. (ILI).

  - Contact: 511 South 7th Street, Delano, MN 55328; Telephone: (763) 972-2981; Fax: (763) 972-2911.

- Other Available Manufacturers – subject to compliance with requirements stated within.

  - (List acceptable equals by name)

2.02	MATERIAL

- Blades and fascia shall be fabricated from a minimum .125 (1/8”) wall thickness extruded aluminum.  Blades shall be of design as indicated on drawings.

- (Tapered) outrigger material shall be fabricated from a minimum .250 (1/4”) wall thickness plate aluminum.

- Mounting brackets shall be fabricated from a minimum .375 (3/8”) wall thickness.

- Aluminum Extrusions: ASTM B221, Alloy 6063-T6

- Fully mechanically fastened construction

##### 2.03	FINISHES (FACTORY)

- General: Comply with NAAMM “Metal Finishes Manual” for finish designations and application recommendations, except as otherwise indicated.  Apply finishes in factory.  Protect finishes on exposed surfaces prior to shipment.  Remove scratches and blemishes from exposed surfaces that will be visible after completing finishing process.  Provide color as indicated or, if not otherwise indicated, as selected by architect.

*NOTE TO SPECIFIER* Please delete finishes not required

- Standard mill finish.

- Prime Coat:

  - Apply alkyd prime coat following chemical cleaning and pretreatment.

  - Primer preparation for field painting.

- Fluorocarbon Two Coat Finish

  - Coating shall conform to AAMA 2605.

  - Sun Control Devices to be finished with a minimum 1.0 mil (0.025 mm) thick full strength 70% resin, 2 coat Fluoropolymer system.

  - All aluminum shall be thoroughly cleaned, etched, and given a chrome-free  conversion pretreatment before application of coating. Coating shall be ILFI LBC Red List Free.

- Fluorocarbon Three Coat Finish

  - Coating shall conform to AAMA 2605.

  - Sun Control Devices to be finished with a minimum 1.4 mil (0.035 mm) thick full strength 70% resin, 3 coat Fluoropolymer system.

  - All aluminum shall be thoroughly cleaned, etched, and given a chrome-free  conversion pretreatment before application of coating. Coating shall be ILFI LBC Red List Free.

- Clear Anodize

  - Class I Clear Anodize

    - Comply with Aluminum Association AA-C22A41.  Clear anodized finish 215-R1.

    - Apply finish following chemical etching and pretreatment

    - Minimum thickness: 0.7 mils (0.018 mm)

  - Class II Clear Anodize

    - Comply with Aluminum Association AA-C22A31.  Clear anodized finish 204-R1.

    - Apply finish following chemical etching and pretreatment

    - Minimum thickness: 0.4 mils (0.01 mm)

- Color Anodize

  - Class I Bronze Anodize

    - Light, Medium, Dark, Champagne

    - Comply with Aluminum Association AA-C2242 or AA-C2244.

    - Apply finish following chemical etching and pretreatment

    - Minimum thickness: 0.7 mils (0.018 mm)

  - Class I Black Anodize

    - Comply with Aluminum Association AA-C2242 or AA-C2244.

    - Apply finish following chemical etching and pretreatment

    - Minimum thickness: 0.7 mils (0.018 mm)

PART 3 EXECUTION

##### EXAMINATION

- Examine substrates for compliance with requirements for installation tolerances and other conditions affecting performance.

- Proceed with installation only after unsatisfactory conditions have been corrected.

  - PREPARATION

- Clean surfaces thoroughly prior to installation.

- Prepare surfaces using methods recommended by the manufacturer for achieving the best results for the substrate under the project conditions.

3.03	INSTALLATION

- Install sun control devices at locations as indicated on the drawings and in accordance with the manufacturer’s instructions.

3.04	CLEANING

- Clean sun control device surface in accordance with manufacturer’s instructions.

- Touch-up paint, repair or replace damaged products before Substantial Completion.